## Facility Summary
Facility Name |  | SN | SE | WN | WE
TLS1
| Most limiting | #REF!
| limiting element | #REF!
Next limiting
Facility Name |  | SN | SE | WN | WE
TLS2
Most limiting
Next limiting

## CAISO Update
Type of Change | OID | Station Name | Component Description | Component Type | High kV | Low kV | Tertiary kV | Length | ISO Control | Units | Additional Information | Line Number | Rating Type | High Rating | Low Rating | Duration | Note # | Rating Type | High Rating | Low Rating | Duration | Note # | Rating Type | High Rating | Low Rating | Duration | Note # | Rating Type | High Rating | Low Rating | Duration | Note #
| 99221 | [TRANSMISSION LINE] | SUB1-SUB2 | TL | 115 |  |  |  | Y | AMPS
Previously Submitted |  | SUB1 | 115 kV MAIN BUS | BUS | 115 |  |  |  | Y | AMPS | 715.5 kcmil AAC-Interior rating |  | SN (N) | 631 |  | 0 |  | SE (A) | 742 |  | 4 |  | WN (B) | 972 |  | 0 |  | WE (C) | 1039 |  | 4
Previously Submitted | 163127 | SUB1 | 1012 | CB | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Previously Submitted | 163114 | SUB1 | 1032 | CB | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 1200 |  | 0 |  | SE (A) | 1200 |  | 4 |  | WN (B) | 1200 |  | 0 |  | WE (C) | 1200 |  | 4
Create |  | SUB1 | CB 1012 | CT | 115 |  |  |  | Y | AMPS | 400/5*2 TRF = 800A; Manufactured 2007 |  | SN (N) | 800 |  | 0 |  | SE (A) | 800 |  | 4 |  | WN (B) | 800 |  | 0 |  | WE (C) | 800 |  | 4
Update | 163115 | SUB1 | CB 1032 | CT | 115 |  |  |  | Y | AMPS | 800/5*1 TRF = 800A; Installed 1995 |  | SN (N) | 800 |  | 0 |  | SE (A) | 800 |  | 4 |  | WN (B) | 800 |  | 0 |  | WE (C) | 800 |  | 4
Previously Submitted | 163125 | SUB1 | 1011 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Previously Submitted | 163126 | SUB1 | 1013 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Previously Submitted | 163113 | SUB1 | 1031 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 600 |  | 0 |  | SE (A) | 600 |  | 4 |  | WN (B) | 600 |  | 0 |  | WE (C) | 600 |  | 4
Previously Submitted | 163112 | SUB1 | 1033 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 600 |  | 0 |  | SE (A) | 600 |  | 4 |  | WN (B) | 600 |  | 0 |  | WE (C) | 600 |  | 4
Previously Submitted | 163111 | SUB1 | 1035 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 163109 | SUB1 | SUB1-SUB2 - CB 1012 & CB 1032 | WTRP | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 163110 | SUB1 | SUB1-SUB2 - CB 1012 & CB 1032 (smallest TERM cond) | COND | 115 |  |  |  | Y | AMPS | 715.5 KCMIL AL - SPECIAL RATING PER 073137 - INTERIOR RATING (715.5 KCMIL AL - SPECIAL RATING PER 073137, 2-1113 KCMIL AL - SPECIAL RATING PER 073137, 3" SPS AL TUBING) |  | SN (N) | 742 |  | 0 |  | SE (A) | 835 |  | 4 |  | WN (B) | 1039 |  | 0 |  | WE (C) | 1100 |  | 4
Update | 163116 | SUB1 | SUB1-SUB2 - CB 1012 & CB 1032 | TERM | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 600 |  | 0 | 11 | SE (A) | 600 |  | 4 | 11 | WN (B) | 600 |  | 0 | 11 | WE (C) | 600 |  | 4 | 11
Update | 118573 | [TRANSMISSION LINE] | SUB1-SUB2 - From Sub1 To 004/037 | TLS | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 390 |  | 0 |  | SE (A) | 456 |  | 4 |  | WN (B) | 589 |  | 0 |  | WE (C) | 600 |  | 4 | 11
Retire | 118572 | [TRANSMISSION LINE] | SUB1-SUB2 - From Sub1 To 039/254B | COND | 115 |  |  | 6.28 | Y | AMPS | CONDUCTOR INFO: 336.4 - 30/7 - ACSR - SINGLE - INTERIOR |  | SN (N) | 449 |  | 0 |  | SE (A) | 512 |  | 4 |  | WN (B) | 647 |  | 0 |  | WE (C) | 687 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From Sub1 To 045/301B | COND | 115 |  |  | 0.02 | Y | AMPS | 715.0-37 - AAC - SINGLE - INTERIOR RATING |  | SN (N) | 631 |  | 0 |  | SE (A) | 742 |  | 4 |  | WN (B) | 972 |  | 0 |  | WE (C) | 1039 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 045/301B To 042/278B | COND | 115 |  |  | 2.76 | Y | AMPS | 397.5-26/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 493 |  | 0 |  | SE (A) | 563 |  | 4 |  | WN (B) | 712 |  | 0 |  | WE (C) | 757 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 042/278B To 042/277B | COND | 115 |  |  | 0.22 | Y | AMPS | 336.4-30/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 449 |  | 0 |  | SE (A) | 512 |  | 4 |  | WN (B) | 647 |  | 0 |  | WE (C) | 687 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 042/277B To 039/255B | COND | 115 |  |  | 2.97 | Y | AMPS | 397.5-26/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 493 |  | 0 |  | SE (A) | 563 |  | 4 |  | WN (B) | 712 |  | 0 |  | WE (C) | 757 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 039/255B To 039/254B | COND | 115 |  |  | 0.31 | Y | AMPS | 336.4-30/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 449 |  | 0 |  | SE (A) | 512 |  | 4 |  | WN (B) | 647 |  | 0 |  | WE (C) | 687 |  | 4
Update | 118571 | [TRANSMISSION LINE] | SUB1-SUB2 - From 039/254B To 036/242B | COND | 115 |  |  | 2.59 | Y | AMPS | CONDUCTOR INFO: 336.4 - 12/7 - ACAR - SINGLE - INTERIOR |  | SN (N) | 390 |  | 0 |  | SE (A) | 456 |  | 4 |  | WN (B) | 589 |  | 0 |  | WE (C) | 630 |  | 4
Update | 118570 | [TRANSMISSION LINE] | SUB1-SUB2 - From 036/242B To 032/221B | COND | 115 |  |  | 4.32 | Y | AMPS | CONDUCTOR INFO: 397.5 - 26/7 - ACSR - SINGLE - INTERIOR |  | SN (N) | 493 |  | 0 |  | SE (A) | 563 |  | 4 |  | WN (B) | 712 |  | 0 |  | WE (C) | 757 |  | 4
Update | 118576 | [TRANSMISSION LINE] | SUB1-SUB2 - From 032/221B To 022/163 | COND | 115 |  |  | 9.62 | Y | AMPS | 336.4-30/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 449 |  | 0 |  | SE (A) | 512 |  | 4 |  | WN (B) | 647 |  | 0 |  | WE (C) | 687 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 022/163 To 020/147 | COND | 115 |  |  | 2.8 | Y | AMPS | 397.5-26/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 493 |  | 0 |  | SE (A) | 563 |  | 4 |  | WN (B) | 712 |  | 0 |  | WE (C) | 757 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 020/147 To 020/146B | COND | 115 |  |  | 0.1 | Y | AMPS | 336.4-30/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 449 |  | 0 |  | SE (A) | 512 |  | 4 |  | WN (B) | 647 |  | 0 |  | WE (C) | 687 |  | 4
Update | 118575 | [TRANSMISSION LINE] | SUB1-SUB2 - From 020/146B To 015/117 | COND | 115 |  |  | 4.78 | Y | AMPS | 336.4-12/7 - ACAR - SINGLE - INTERIOR RATING |  | SN (N) | 390 |  | 0 |  | SE (A) | 456 |  | 4 |  | WN (B) | 589 |  | 0 |  | WE (C) | 630 |  | 4
Create |  | [TRANSMISSION LINE] | SUB1-SUB2 - From 015/117 To 004/037 | COND | 115 |  |  | 10.58 | Y | AMPS | 397.5-26/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 493 |  | 0 |  | SE (A) | 563 |  | 4 |  | WN (B) | 712 |  | 0 |  | WE (C) | 757 |  | 4
Retire |  | [TRANSMISSION LINE] | SUB1-SUB2 - From SUB1 To 004/037 - Switch 107 | DISC | 115 |  |  |  | Y | AMPS | Switch 107 located at 012/096A |  | SN (N) | 600 |  | 0 |  | SE (A) | 600 |  | 4 |  | WN (B) | 600 |  | 0 |  | WE (C) | 600 |  | 4
Retire | 118574 | [TRANSMISSION LINE] | SUB1-SUB2 - From SUB1 Sub To 4/7 - #117 | DISC | 115 |  |  |  | Y | AMPS | 117 |  | SN (N) | 600 |  | 0 | 22 | SE (A) | 600 |  | 4 | 22 | WN (B) | 600 |  | 0 | 22 | WE (C) | 600 |  | 4 | 22
Retire |  | [TRANSMISSION LINE] | SUB1-SUB2 - From SUB1 To 004/037 - Switch 119 | DISC | 115 |  |  |  | Y | AMPS | Switch 119 located at 041/268 |  | SN (N) | 600 |  | 0 |  | SE (A) | 600 |  | 4 |  | WN (B) | 600 |  | 0 |  | WE (C) | 600 |  | 4
Previously Submitted | 186805 | [TRANSMISSION LINE] | SUB1-SUB2 - From SUB1 To 004/037 - Switch 329 | DISC | 115 |  |  |  | Y | AMPS | Switch 329 located at 004/038 |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 118577 | [TRANSMISSION LINE] | SUB1-SUB2 - From 004/037 To SUB2 | TLS | 115 |  |  |  | Y | AMPS |  |  | SE (A) | 400 |  | 0 | 27 | SE (A) | 400 |  | 4 | 27 | WN (B) | 400 |  | 0 | 27 | WE (C) | 400 |  | 4 | 27
Update | 118578 | [TRANSMISSION LINE] | SUB1-SUB2 - From 004/037 To SUB2 | COND | 115 |  |  | 4.82 | Y | AMPS | 397.5-26/7 - ACSR - SINGLE - INTERIOR RATING |  | SN (N) | 493 |  | 0 |  | SE (A) | 563 |  | 4 |  | WN (B) | 712 |  | 0 |  | WE (C) | 757 |  | 4
Previously Submitted | 186806 | [TRANSMISSION LINE] | SUB1-SUB2 - From 004/037 To SUB2 - Switch 327 | DISC | 115 |  |  |  | Y | AMPS | Switch 327 located at 004/036 |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 173428 | SUB2 | 115 kV BUS 1 | BUS | 115 |  |  |  | Y | AMPS | 2" IPS CU - INTERIOR RATING (2" IPS CU, 2-2300 KCMIL AL, 4" AL Tube - SCH 80) |  | SN (N) | 1770 |  | 0 |  | SE (A) | 2235 |  | 4 |  | WN (B) | 2445 |  | 0 |  | WE (C) | 2805 |  | 4
Update | 182003 | SUB2 | 115 kV BUS 2 | BUS | 115 |  |  |  | Y | AMPS | 2" IPS CU - INTERIOR RATING (2" IPS CU, 2-2300 KCMIL AL, 4" AL Tube - SCH 80) |  | SN (N) | 1770 |  | 0 |  | SE (A) | 2235 |  | 4 |  | WN (B) | 2445 |  | 0 |  | WE (C) | 2805 |  | 4
| 96655 | SUB2 | 132 | CB | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 166651 | SUB2 | CB 132 | CT | 115 |  |  |  | Y | AMPS | 1000/5*2 TRF = 2000A; Installed 2002 |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Create |  | SUB2 | 131 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 155179 | SUB2 | 133 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
Update | 155180 | SUB2 | 135 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 2000 |  | 0 |  | SE (A) | 2000 |  | 4 |  | WN (B) | 2000 |  | 0 |  | WE (C) | 2000 |  | 4
| 155181 | SUB2 | 137 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 600 |  | 0 |  | SE (A) | 600 |  | 4 |  | WN (B) | 600 |  | 0 |  | WE (C) | 600 |  | 4
| 155182 | SUB2 | 139 | DISC | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 600 |  | 0 |  | SE (A) | 600 |  | 4 |  | WN (B) | 600 |  | 0 |  | WE (C) | 600 |  | 4
Update | 166652 | SUB2 | SUB1-SUB2 - CB 132 | WTRP | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 400 |  | 0 |  | SE (A) | 400 |  | 4 |  | WN (B) | 400 |  | 0 |  | WE (C) | 400 |  | 4
Update | 166650 | SUB2 | SUB1-SUB2 - CB 132 (smallest TERM cond) | COND | 115 |  |  |  | Y | AMPS | SN/WN 3/4" IPS CU; SE/WE 715 KCMIL AL - SPECIAL RATING PER 073137 - INTERIOR RATINGS (3/4" IPS CU, 715 KCMIL AL - SPECIAL RATING PER 073137, 1113 KCMIL AL - SPECIAL RATING PER 073137) |  | SN (N) | 725 |  | 0 |  | SE (A) | 835 |  | 4 |  | WN (B) | 1005 |  | 0 |  | WE (C) | 1100 |  | 4
Update | 166653 | SUB2 | SUB1-SUB2 - CB 132 | TERM | 115 |  |  |  | Y | AMPS |  |  | SN (N) | 400 |  | 0 | 27 | SE (A) | 400 |  | 4 | 27 | WN (B) | 400 |  | 0 | 27 | WE (C) | 400 |  | 4 | 27
Required Updates

## Source Doc Ref Tbl
Station Name | Component Description | Component Type | Celerity Analysis Comments | High Rating
[TRANSMISSION LINE] | TRINITY-COTTONWOOD | TL
TRINITY | 115 kV MAIN BUS | BUS | GAD 346000 Rev 14; BOM 043676 Rev 8 Sheet 8, Item 39; Verified per Pro-E AID 1370 | 631
TRINITY | 1012 | CB | SLD 329648 Rev 13; Verified per Pro-E AID 1371 | 2000
TRINITY | 1032 | CB | SLD 329648 Rev 13; Verified per Pro-E AID 1373 | 1200
TRINITY | CB 1012 | CT | Verified in Powerbase by RQHG | 800
TRINITY | CB 1032 | CT | Verified in Powerbase by RQHG | 800
TRINITY | 1011 | DISC | Previously Submitted on Humboldt-Trinity 115 kV on 3/16/2021; Verified per Pro-E AID 1374 | 2000
TRINITY | 1013 | DISC | Previously Submitted on Humboldt-Trinity 115 kV on 3/16/2021; Verified per Pro-E AID 1375 | 2000
TRINITY | 1031 | DISC | Previously Submitted on Humboldt-Trinity 115 kV on 3/16/2021; Verified per Pro-E AID 1378 | 600
TRINITY | 1033 | DISC | Previously Submitted on Humboldt-Trinity 115 kV on 3/16/2021; Verified per Pro-E AID 1379 | 600
TRINITY | 1035 | DISC | Previously Submitted on Humboldt-Trinity 115 kV on 3/16/2021; Verified per Pro-E AID 1380 | 2000
TRINITY | TRINITY-COTTONWOOD - CB 1012 & CB 1032 | WTRP | GAD 4049362 Rev 4; BOM 043676 Rev 11 Sheet 43, Item 166 | 2000
TRINITY | TRINITY-COTTONWOOD - CB 1012 & CB 1032 (smallest TERM cond) | COND | GAD 4049362 Rev 4; BOM 043676 Rev 11 Sheet 46, Item 184; Compression Fitting: BOM 043676 Rev 11 Sheet 48, Item 190 | 742
TRINITY | TRINITY-COTTONWOOD - CB 1012 & CB 1032 | TERM | 11. Limited by multiple components | 600
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From Trinity To 004/037 | TLS | 115 | 390
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From Trinity To 045/301B | COND | 115 | 631
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 045/301B To 042/278B | COND | 115 | 493
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 042/278B To 042/277B | COND | 115 | 449
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 042/277B To 039/255B | COND | 115 | 493
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 039/255B To 039/254B | COND | 115 | 449
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 039/254B To 036/242B | COND | 115 | 390
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 036/242B To 032/221B | COND | 115 | 493
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 032/221B To 022/163 | COND | 115 | 449
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 022/163 To 020/147 | COND | 115 | 493
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 020/147 To 020/146B | COND | 115 | 449
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 020/146B To 015/117 | COND | 115 | 390
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 015/117 To 004/037 | COND | 115 | 493
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From Trinity To 004/037 - Switch 329 | DISC | 115 | 2000
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 004/037 To Cottonwood | TLS | 115 | 400
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 004/037 To Cottonwood | COND | 115 | 493
[TRANSMISSION LINE] | TRINITY-COTTONWOOD - From 004/037 To Cottonwood - Switch 327 | DISC | 115 | 2000
COTTONWOOD | 115 kV BUS 1 | BUS | Previously Submitted on Cascade-Cottonwood on 11/17/2019; GAD 4035234 Rev 4; BOM 027258 Rev 26 Sheet 72, Item 278 | 2990
COTTONWOOD | 115 kV BUS 2 | BUS | Previously Submitted on Cascade-Cottonwood on 11/17/2019; GAD 4035234 Rev 4; BOM 027258 Rev 26 Sheet 72, Item 278 | 2990
COTTONWOOD | 132 | CB | GAD 402523 Rev 23; BOM 023910 Rev 15 Sheet 31, Item 130 | 2000
COTTONWOOD | CB 132 | CT | Verified in Powerbase by RQHG | 2000
COTTONWOOD | 131 | DISC | GAD 402523 Rev 23; BOM 023910 Rev 21 Sheet 60, Item 282 | 2000
COTTONWOOD | 133 | DISC | GAD 402523 Rev 23; BOM 023910 Rev 21 Sheet 60, Item 283 | 2000
COTTONWOOD | 135 | DISC | GAD 402523 Rev 23; BOM 023910 Rev 21 Sheet 60, Item 284 | 2000
COTTONWOOD | 137 | DISC | SLD 55229 Rev 79; Verified by SAP Database ARSW Dec 2022, 40976135 | 600
COTTONWOOD | 139 | DISC | SLD 55229 Rev 79; Verified by SAP Database ARSW Dec 2022, 40976141 | 600
COTTONWOOD | TRINITY-COTTONWOOD - CB 132 | WTRP | GAD 322539 Rev 7; BOM 034442 Rev 10 Sheet 1A, Item 3 | 400
COTTONWOOD | TRINITY-COTTONWOOD - CB 132 (smallest TERM cond) | COND | GAD 322539 Rev 7; GAD 402523 Rev 23; For 715 KCMIL AL Compression Fittings: BOM 034442 Rev 11 Sheet 14, Item 62 | 725
COTTONWOOD | TRINITY-COTTONWOOD - CB 132 | TERM | 27. Limited by Wave Trap rating | 400

## Calcs
Find line current based on Line to Line kV and 3 phase MVA |  |  |  | Find line MVA based on Line to Line kV and line current |  |  |  | Find Line to Neutral kV based on Line to Line kV
kVLL | 60 | 115 | 70 | kVLL | 60 | 70 | 115 | kVLL | 60 | 115
Rated MVA | 62.4 | 82.9 | 14.2 | I | 300 | 400 | 416 | kVLN | 34.641 | 66.3953
I | 600.4443 | 416.1942 | 117.1196 | MVA | 31.1769 | 48.4974 | 82.8613